## Internal Connections
Narrative: Internally build Single Mode Fiber Backbone covering all racks. with state of the art structured cable management
Utilizing new wall-mounted racks near existing racks, Fiber terminations of 12 pair to each rack identified as IDF which are integrated in to MPO type cabinets to allow 400GB
All Copper will be re-pulled in entire building to use Blue Cat6. Cable ladders, Management/ Ladders/Signage will be required
Use existing Drops at end points if available (in wall boxes, or existing raceway) New Cat 6 Green Keystones and remove abandoned wiring
Goal: Future Proof the wiring infrastructure for 25 years.
Fiber will run from each MDF to every IDF rack to provide 100GB backbone throughout buildings
New Wall mount racks will be required for MDF/IDF racks, including top 1u termination of fiber and Rack mounted UPS
item | desc | capability | qty | features
Admin BLD
Internet drop and WAN Connection point |  |  | 128 | 1gb POE
916 Hwy 64 East | Copper Wiring | cat 6+ | 100 | fully structured with racks/ladders/cable management
100 drops new construction planned Jan 2022
UPS in rack or at least off the floor
Annex | 4 slot chassis | 10GB, 40GB, 100GB capable | 2 | 8 port Fiber Modules populated with SFP+
current data center, must mirror fiber ports to transport fiber from POP to DC. then back to Distribution Point | use existing racks (cabinets) |  | 96 | 1gbe POE
25 drops
AMS | rack 1/4 upper library | MDF
716 Hwy 64 East | 12 slot chassis | 10GB, 40GB, 100GB capable | 4 | Fiber Ports populated with SFP+
300 drops | rack 2/4 Office
| Switch/Stack of | 10GB, 40GB, 100GB capable | 1 | Fiber Port
|  |  | 96 | 1gbe POE
| rack 3/4 f hall | IDF
| Switch/Stack of | 10GB, 40GB, 100GB capable | 1 | Fiber Port
|  |  | 48 | 1gbe POE
rack 4/4 laundry
| Switch/Stack of | 10GB, 40GB, 100GB capable | 1 | Fiber Port
|  |  | 24 | 1gbe POE
APS | rack 1/2 Office | MDF
1600 Hwy 64 East | Switch/Stack of | 10GB, 40GB, 100GB capable | 4 | Fiber Port
200 drops |  |  | 96 | 1gbe POE
| rack 2/2 E Hall | IDF
| Switch/Stack of | 10GB, 40GB, 100GB capable | 1 | Fiber Port
|  |  | 48 | 1gbe POE
AIS | rack 1/2 Library | MDF
1220 Collum Lane | Switch/Stack of | 10GB, 40GB, 100GB capable | 4 | Fiber Port
250 drops |  |  | 96 | 1gbe POE
| rack 2/2 C Hall | IDF
| Switch/Stack of | 10GB, 40GB, 100GB capable | 1 | Fiber Port
|  |  | 48 | 1gbe POE
AHS | rack 1/13 Office | MDF
101 E Main ST | 12 slot chassis | 10GB, 40GB, 100GB capable | 24 | Fiber Port
| 96 DROPS |  | 96 | 1gbe POE
| rack 2/14 1400 | IDF
| 12 slot chassis | 10GB, 40GB, 100GB capable | 8 | Fiber Port
| 120 drops |  | 128 | 1gbe POE
| rack 3/14 110 | IDF
| Switch/Stack of | 10GB, 40GB, 100GB capable | 1 | Fiber Port
| 200 DROPS |  | 128 | 1gbe POE
rack 3/14 Green Room
| Switch/Stack of | 10GB, 40GB, 100GB capable | 1 | Fiber Port
| 12 drops |  | 24 | 1gbe POE
| rack 5/14 Fieldhouse | IDF
| Switch/Stack of | 10GB, 40GB, 100GB capable | 8 | Fiber Port
| 48 drops |  | 48 | 1gbe POE
rack 6/14 AOS
| Switch/Stack of | 10GB, 40GB, 100GB capable | 1 | Fiber Port
| 16 drops |  | 24 | 1gbe POE
rack 7/14 PressBox
| Switch/Stack of | 10GB, 40GB, 100GB capable | 1 | Fiber Port
| 20 drops |  | 24 | 1gbe POE
New Construction 2021 | rack 8/14 Agri
| Switch/Stack of | 10GB, 40GB, 100GB capable | 8 | Fiber Port
| 100 drops |  | 64 | 1gbe POE
| rack 9/14 1105 | idf
| Switch/Stack of | 10GB, 40GB, 100GB capable | 8 | Fiber Port
| 24 drops |  | 24 | 1gbe POE
rack 10/14 ROTC
| Switch/Stack of | 10GB, 40GB, 100GB capable | 1 | Fiber Port
| 12 drops |  | 64 | 1gbe POE
| rack 11/14 Water Room | IDF
| Switch/Stack of | 10GB, 40GB, 100GB capable | 8 | Fiber Port
| 96 drops |  | 24 | 1gbe POE
| rack 12/14 805 | IDF
| Switch/Stack of | 10GB, 40GB, 100GB capable | 8 | Fiber Port
| 60 drops |  | 24 | 1gbe POE
rack 13/14 SW Arena
| Switch/Stack of | 10GB, 40GB, 100GB capable | 1 | Fiber Port
| 15 drops |  | 24 | 1gbe POE
New Construction 2021 | rack 14/14 Activity Center
| Switch/Stack of | 10GB, 40GB, 100GB capable | 1 | Fiber Port
| 64 drops |  | 64 | 1gbe POE

## Fiber Specs
General Fiber Spec
This section specifies the component requirements for an optical fiber cabling system (cable, patch panels, connectors, patch cords, etc.) for both horizontal and backbone cabling. All Glass in fiber optic trunking, cassette modules, and jumpers MUST be Corning Clear Curve Laser Optimized BIF Multimode OM4 multimode fiber and OS2 BIF Single mode fiber, and must be CABLExpress Skinny Trunk Product or Equivalent
Preterminated MTP trunks must utilize sub-unitized construction for maximum flexibility.
Pulling socks that withstand a minimum of 200 lbs pulling force, connectorized ends tested to ensure loss does not increase over 1dB for axial pull of 2.5lb/ft. and off axial 7lb/ft.
All assemblies tested with overfilled launch condition and a VCSEL source. This ensures entire core of fiber can meet test criteria, not just one section. Test data must ship with the trunks and must reflect the number of the VCSEL test.
Maximum insertion loss for MTP® connector is 0.35dB/mated pair, for LC is 0.15dB/per mated pair.
Maximum insertion loss for entire MTP®-LC cassette is 0.5dB
End face geometry tested for tilt, height, adjacent differential, maximum height and core dip.
Environmental testing performed to cover temperature and humidity, heat aging, thermal cycling, thermal shock, temperature functionality.
The MTP® post polish end face geometry shall be within the following:
Tilt on long and short angles - Long and short angles tilt must be within -0.2° min and 0.2° max
IEC61300-3-35 covers all the below in RED
Fiber height - Fiber height must be within 1000 nm min and 3000 nm max
Adjacent differential - The adjacent differential must not exceed 250 nm. This is the height difference of any given fibers as compared to its adjacent fiber(s).
Maximum height - Minimum height of the 12 fibers measured; the maximum height measured subtracted from the minimum height measured must not exceed 500 nm.
Core dip (Fiber) - Core dip must be within -100nm min to 100 nm max.
Off Axial Pull: LC connectors must be built to mechanically withstand an off axial pull of 133N (30lb/f).
Only MTP® connectors from US Conec are used. In addition, only elite ferrules are used (improves core alignment).
All glass is Corning Bend Insensitive Fiber (BIF)
Must also meet or exceed the follow standards and documentation included
· TIA/EIA 568A/B/C/D
· TIA/EIA 604, 604-5, 604-10, 604-12, 604-13
· FOTP-203 Encircled Flux Measurement of Multi-mode Fiber
· GR-326 AND GR-1435
· IBM 960001ML, 44P229, P51H998, P11P1912, P5460451, 0855995, 5454620, AND 46G3772
All cable and connecting hardware shall meet the requirements of the applicable codes in that jurisdiction.

## Data Center-Backbone Fiber Spec
Data Center Backbone Optical Fiber Cable
General
Covered herein are the detailed specifications of the optical fiber cable for use in the data center backbone cabling.
Fiber Optic Cable Riser Rated Building Solutions
Approved Multimode Plenum Rated fiber optic building cables: No Substitutions
OM4 Bend Insensitive Multimode Fiber Optic Cable
CABLExpress Skinny Trunk NON Armored Skinny- Trunk MTP-MTP (12 – 144 fibers)
CABLExpress Skinny Trunk Armored Skinny- Trunk MTP-MTP (12 – 144 fibers)
Approved Single-Mode Fiber Optic Cable
OS2 Bend Insensitive Single Mode Fiber Optic Cable
CABLExpress Skinny Trunk NON Armored Skinny- Trunk MTP-MTP (12 – 144 fibers)
CABLExpress Skinny- Trunk MTP-MTP (12 – 144 fibers)
CABLExpress Fiber Optic Termination Shelf
Approved CABLExpress RSD Modular Shelf :
1U configuration for up to 48 duplex LC ports p/n# CBX-FE-1U4
2U configuration for up to 96 duplex LC ports p/n# CBX-FE-2U8
4U configuration for up to 192 duplex LC ports p/n# CBX-FE-4U16